## Sheet1
Calendar Year | Fiscal Year | Month | MonthNum | Date | Days | Hours | FYQTR | Waste Collected (tons) | Waste Processed (tons) | Waste Processed (klbs) | Steam (klbs) | Average Steam Production (klbs/hour) | Gross Steam Production Ratio (klbs-steam/klbs-refuse) | Ash Removal (tons) | Special Handling (tons) | Ferrous Recovered (tons) | Column1 | Net Refuse (klbs) | Net Steam Production Ratio (klbs-steam/klbs-net-refuse) | Daily Waste Collection (tons/day) | HHVcalculated,avg (Btu/lb) | HHVcalculated,qtr_avg (Btu/lb) | HHVcalculated,annuak_avg (Btu/lb) | Net Electrical Generation (MWh) | Gross Electrical Production (MWh) | Average Steam Temperature (F) | Purchased Power (MWh) | Fuel Oil (gal) | Boiler Make-up Water (gal) | Boiler Make-up % of Steam | Cooling Tower Make-up Water (gal) | Boiler 1 Availability (%) | Boiler 2 Availability (%) | Boiler 3 Availability (%) | Turbine 1 Availability (%) | Turbine 2 Availability (%) | Boiler Unscheduled Downtime | Boiler Scheduled Downtime | Boiler Standby Downtime | Turbine Unscheduled Downtime | Turbine Scheduled Downtime | Turbine Standby Downtime | U1-Steam Flow AVG | U1-Steam Flow MAX | U1-Steam Flow MIN | U2-Steam Flow AVG | U2-Steam Flow MAX | U2-Steam Flow MIN | U3-Steam Flow AVG | U3-Steam Flow MAX | U3-Steam Flow MIN
2009 | 2009 | January | 1 | 3981400% | 31 | 744 | 3 |  | 29063 | 58126 | 186003 | 250.004 | 3.2 |  |  |  | 0 | 58126 | 3.2 | 0
2009 | 2009 | February | 2 | 3984500% | 28 | 672 | 3 |  | 25040 | 50080 | 167268 | 248.9107 | 3.34 |  |  |  | 0 | 50080 | 3.34 | 0
2009 | 2009 | March | 3 | 3987300% | 31 | 744 | 3 |  | 27347 | 54694 | 171740 | 230.8333 | 3.14 |  |  |  | 0 | 54694 | 3.14 | 0
2009 | 2009 | April | 4 | 3990400% | 30 | 720 | 4 |  | 29566 | 59132 | 185674 | 257.8806 | 3.14 |  |  |  | 0 | 59132 | 3.14 | 0
2009 | 2009 | May | 5 | 3993400% | 31 | 744 | 4 |  | 30883 | 61766 | 182829 | 245.7379 | 2.96 |  |  |  | 0 | 61766 | 2.96 | 0
2009 | 2009 | June | 6 | 3996500% | 30 | 720 | 4 |  | 29433 | 58866 | 167770 | 233.0139 | 2.85 |  |  |  | 0 | 58866 | 2.85 | 0
2009 | 2010 | July | 7 | 3999500% | 31 | 744 | 1 |  | 28103 | 56206 | 175629 | 236.0605 | 3.1247 |  |  |  | 0 | 56206 | 3.1247 | 0
2009 | 2010 | August | 8 | 4002600% | 31 | 744 | 1 |  | 29921 | 59842 | 178109 | 239.3938 | 2.9763 |  |  |  | 0 | 59842 | 2.9763 | 0
2009 | 2010 | September | 9 | 4005700% | 30 | 720 | 1 |  | 25477 | 50954 | 161523 | 224.3375 | 3.17 |  |  |  | 0 | 50954 | 3.17 | 0
2009 | 2010 | October | 10 | 4008700% | 31 | 744 | 2 |  | 27642 | 55284 | 158112 | 212.5161 | 2.86 |  |  |  | 0 | 55284 | 2.86 | 0
2009 | 2010 | November | 11 | 4011800% | 30 | 720 | 2 |  | 26973 | 53946 | 157048 | 218.1222 | 2.9112 |  |  |  | 0 | 53946 | 2.9112 | 0
2009 | 2010 | December | 12 | 4014800% | 31 | 744 | 2 |  | 26262 | 52524 | 167476 | 225.1022 | 3.1886 |  |  |  | 0 | 52524 | 3.1886 | 0
2010 | 2010 | January | 1 | 4017900% | 31 | 744 | 3 |  | 26555 | 53110 | 166236 | 223.4355 | 3.13 |  |  |  | 0 | 53110 | 3.13 | 0
2010 | 2010 | February | 2 | 4021000% | 28 | 672 | 3 |  | 20751 | 41502 | 119939 | 178.4807 | 2.89 |  |  |  | 0 | 41502 | 2.89 | 0
2010 | 2010 | March | 3 | 4023800% | 31 | 744 | 3 |  | 27827 | 55654 | 171779 | 230.8858 | 3.0866 |  |  |  | 0 | 55654 | 3.0866 | 0
2010 | 2010 | April | 4 | 4026900% | 30 | 720 | 4 |  | 30400 | 60800 | 190052 | 263.9611 | 3.1259 |  |  |  | 0 | 60800 | 3.1259 | 0
2010 | 2010 | May | 5 | 4029900% | 31 | 744 | 4 |  | 29189 | 58378 | 182511 | 245.3105 | 3.1264 |  |  |  | 0 | 58378 | 3.1264 | 0
2010 | 2010 | June | 6 | 4033000% | 30 | 720 | 4 |  | 30481 | 60962 | 189282 | 262.8917 | 3.1049 |  |  |  | 0 | 60962 | 3.1049 | 0
2010 | 2011 | July | 7 | 4036000% | 31 | 744 | 1 | 32205 | 32366 | 64732 | 195479 | 262.7406 | 3.0198 |  |  |  | 32205 | 64732 | 3.0198 | 1038.871
2010 | 2011 | August | 8 | 4039100% | 31 | 744 | 1 | 33254 | 32636 | 65272 | 191415 | 257.2782 | 2.9326 |  |  |  | 33254 | 65272 | 2.9326 | 1072.7097
2010 | 2011 | September | 9 | 4042200% | 30 | 720 | 1 | 29808 | 29538 | 59076 | 176635 | 245.3264 | 2.99 |  |  |  | 29808 | 59076 | 2.99 | 993.6
2010 | 2011 | October | 10 | 4045200% | 31 | 744 | 2 | 27593 | 28960 | 57920 | 184673 | 248.2164 | 3.1884 |  |  |  | 27593 | 57920 | 3.1884 | 890.0968
2010 | 2011 | November | 11 | 4048300% | 30 | 720 | 2 | 27995 | 28278 | 56556 | 179848 | 249.7889 | 3.18 |  |  |  | 27995 | 56556 | 3.18 | 933.1667
2010 | 2011 | December | 12 | 4051300% | 31 | 744 | 2 | 28848 | 27258 | 54516 | 176290 | 236.9489 | 3.2337 |  |  |  | 28848 | 54516 | 3.2337 | 930.5806
2011 | 2011 | January | 1 | 4054400% | 31 | 744 | 3 | 29298 | 28988 | 57976 | 171508 | 230.5215 | 2.9583 |  |  |  | 29298 | 57976 | 2.9583 | 945.0968
2011 | 2011 | February | 2 | 4057500% | 28 | 672 | 3 | 22262 | 22294 | 44588 | 135199 | 201.189 | 3.0322 |  |  |  | 22262 | 44588 | 3.0322 | 795.0714
2011 | 2011 | March | 3 | 4060300% | 31 | 744 | 3 | 26763 | 27178 | 54356 | 163597 | 219.8884 | 3.0097 |  |  |  | 26763 | 54356 | 3.0097 | 863.3226
2011 | 2011 | April | 4 | 4063400% | 30 | 720 | 4 | 28803 | 29570 | 59140 | 181991 | 252.7653 | 3.0773 |  |  |  | 28803 | 59140 | 3.0773 | 960.1
2011 | 2011 | May | 5 | 4066400% | 31 | 744 | 4 | 33328 | 31565 | 63130 | 174465 | 234.496 | 2.7636 |  |  |  | 33328 | 63130 | 2.7636 | 1075.0968
2011 | 2011 | June | 6 | 4069500% | 30 | 720 | 4 | 29044 | 28562 | 57124 | 174520 | 242.3889 | 3.0551 |  |  |  | 29044 | 57124 | 3.0551 | 968.1333
2011 | 2012 | July | 7 | 4072500% | 31 | 744 | 1 | 23023 | 29652 | 59304 | 194649 | 261.625 | 3.2822 | 7258 | 10 | 647 | 22366 | 43474 | 4.4774 | 742.6774
2011 | 2012 | August | 8 | 4075600% | 31 | 744 | 1 | 33654 | 32130 | 64260 | 183063 | 246.0524 | 2.8488 | 7003 | 10 | 671 | 32973 | 48892 | 3.7442 | 1085.6129
2011 | 2012 | September | 9 | 4078700% | 30 | 720 | 1 | 32641 | 31347 | 62694 | 168735 | 234.3542 | 2.6914 | 6285 | 34 | 748 | 31859 | 48560 | 3.4748 | 1088.0333
2011 | 2012 | October | 10 | 4081700% | 31 | 744 | 2 | 27599 | 29386 | 58772 | 187371 | 251.8427 | 3.1881 | 6997 | 15 | 832 | 26752 | 43084 | 4.349 | 890.2903
2011 | 2012 | November | 11 | 4084800% | 30 | 720 | 2 | 29514 | 28233 | 56466 | 171864 | 238.7 | 3.0437 | 6512 | 15 | 732 | 28767 | 41948 | 4.0971 | 983.8
2011 | 2012 | December | 12 | 4087800% | 31 | 744 | 2 | 29132 | 30264 | 60528 | 187230 | 251.6532 | 3.0933 | 7041 | 21 | 784 | 28327 | 44836 | 4.1759 | 939.7419
2012 | 2012 | January | 1 | 4090900% | 31 | 744 | 3 | 26490 | 25711 | 51422 | 162221 | 218.039 | 3.1547 | 6030 | 12 | 671 | 25807 | 37996 | 4.2694 | 854.5161
2012 | 2012 | February | 2 | 4094000% | 29 | 696 | 3 | 25672 | 25813 | 51626 | 162605 | 233.6279 | 3.1497 | 6220 | 22 | 695 | 24955 | 37752 | 4.3072 | 885.2414
2012 | 2012 | March | 3 | 4096900% | 31 | 744 | 3 | 27729 | 27175 | 54350 | 166470 | 223.75 | 3.0629 | 6373 | 15 | 630 | 27084 | 40314 | 4.1293 | 894.4839
2012 | 2012 | April | 4 | 4100000% | 30 | 720 | 4 | 28390 | 28383 | 56766 | 177252 | 246.1833 | 3.1225 | 6721 | 23 | 642 | 27725 | 41994 | 4.2209 | 946.3333
2012 | 2012 | May | 5 | 4103000% | 31 | 744 | 4 | 31539 | 31623 | 63246 | 183629 | 246.8132 | 2.9034 | 6762 | 68 | 676 | 30795 | 48234 | 3.807 | 1017.3871
2012 | 2012 | June | 6 | 4106100% | 30 | 720 | 4 | 28629 | 28738 | 57476 | 176120 | 244.6111 | 3.0642 | 6222 | 91 | 746 | 27792 | 43358 | 4.062 | 954.3
2012 | 2013 | July | 7 | 4109100% | 31 | 744 | 1 | 29928 | 30390 | 60780 | 184330 | 247.7554 | 3.0327 | 6185 | 151 | 732 | 29045 | 46644 | 3.9518 | 965.4194 |  |  | 4935
2012 | 2013 | August | 8 | 4112200% | 31 | 744 | 1 | 29683 | 29376 | 58752 | 184057 | 247.3884 | 3.1328 | 6437 | 11 | 786 | 28886 | 44284 | 4.1563 | 957.5161 |  |  | 4935
2012 | 2013 | September | 9 | 4115300% | 30 | 720 | 1 | 27241 | 25930 | 51860 | 150515 | 209.0486 | 2.9023 | 5348 | 80 | 669 | 26492 | 39666 | 3.7946 | 908.0333 |  |  | 4935
2012 | 2013 | October | 10 | 4118300% | 31 | 744 | 2 | 27942 | 28661 | 57322 | 186789 | 251.0605 | 3.2586 | 6205 | 25 | 852 | 27065 | 43158 | 4.328 | 901.3548 |  | 5098 | 4935
2012 | 2013 | November | 11 | 4121400% | 30 | 720 | 2 | 28167 | 29144 | 58288 | 180656 | 250.9111 | 3.0994 | 6146 | 234 | 837 | 27096 | 43854 | 4.1195 | 938.9 |  | 5098 | 4935
2012 | 2013 | December | 12 | 4124400% | 31 | 744 | 2 | 25753 | 27017 | 54034 | 179194 | 240.8522 | 3.3163 | 6040 | 405 | 740 | 24608 | 39664 | 4.5178 | 830.7419 |  | 5098 | 4935
2013 | 2013 | January | 1 | 4127500% | 31 | 744 | 3 | 29507 | 28610 | 57220 | 176575 | 237.332 | 3.0859 | 6050 | 363 | 786 | 28358 | 42822 | 4.1235 | 951.8387 |  |  | 4935
2013 | 2013 | February | 2 | 4130600% | 28 | 672 | 3 | 27388 | 26598 | 53196 | 167519 | 249.2842 | 3.1491 | 5458 | 365 | 751 | 26272 | 40048 | 4.183 | 978.1429 |  |  | 4935
2013 | 2013 | March | 3 | 4133400% | 31 | 744 | 3 | 25552 | 26384 | 52768 | 174354 | 234.3468 | 3.3042 | 5751 | 76 | 672 | 24804 | 39770 | 4.3841 | 824.2581 |  |  | 4935
2013 | 2013 | April | 4 | 4136500% | 30 | 720 | 4 | 33231 | 32147 | 64294 | 196219 | 272.5264 | 3.0519 | 6844 | 403 | 731 | 32097 | 48338 | 4.0593 | 1107.7 |  | 4733 | 4935 | 14536
2013 | 2013 | May | 5 | 4139500% | 31 | 744 | 4 | 32293 | 32682 | 65364 | 193668 | 260.3065 | 2.9629 | 6817 | 281 | 775 | 31237 | 49618 | 3.9032 | 1041.7097 |  | 4733 | 4935 | 14186
2013 | 2013 | June | 6 | 4142600% | 30 | 720 | 4 | 30429 | 30851 | 61702 | 180325 | 250.4514 | 2.9225 | 6165 | 271 | 732 | 29426 | 47366 | 3.8071 | 1014.3 |  | 4733 | 4935 | 12669
2013 | 2014 | July | 7 | 4145600% | 31 | 744 | 1 | 32237 | 31409 | 62818 | 185488 | 249.3118 | 2.9528 | 6249 | 546 | 764 | 30927 | 47700 | 3.8886 | 1039.9032 |  |  | 4720 | 12755
2013 | 2014 | August | 8 | 4148700% | 31 | 744 | 1 | 29053 | 29000 | 58000 | 176948 | 237.8333 | 3.0508 | 6206 | 676 | 682 | 27695 | 42872 | 4.1274 | 937.1935 |  |  | 4720 | 12208
2013 | 2014 | September | 9 | 4151800% | 30 | 720 | 1 | 26768 | 26475 | 52950 | 157535 | 218.7986 | 2.9752 | 5712 | 248 | 597 | 25923 | 39836 | 3.9546 | 892.2667 |  |  | 4720 | 10672
2013 | 2014 | October | 10 | 4154800% | 31 | 744 | 2 | 28779 | 27989 | 55978 | 165840 | 222.9032 | 2.9626 | 5763 | 410 | 658 | 27711 | 42316 | 3.9191 | 928.3548 |  | 4771 | 4720 | 11198 | 40089 |  | 5618 | 17140 | 2034000 |  | 29601856
2013 | 2014 | November | 11 | 4157900% | 30 | 720 | 2 | 26340 | 28043 | 56086 | 179483 | 249.2819 | 3.2001 | 6008 | 188 | 689 | 25463 | 42316 | 4.2415 | 878 |  | 4771 | 4720 | 9705 | 40089 |  | 5618 | 17140 | 2034000 |  | 29601856
2013 | 2014 | December | 12 | 4160900% | 31 | 744 | 2 | 30380 | 29253.7 | 58507.4 | 172645 | 232.0497 | 2.9508 | 6062 | 268 | 680 | 29432 | 44487.4 | 3.8808 | 980 |  | 4771 | 4720 | 12165 | 40089 |  | 5618 | 17140 | 2034000 |  | 29601856
2014 | 2014 | January | 1 | 4164000% | 31 | 744 | 3 | 28241 | 28329 | 56658 | 174634 | 234.7231 | 3.0822 | 5956 | 276 | 834 | 27131 | 42526 | 4.1065 | 911 |  | 4752 | 4720 | 12523 | 41990 |  | 6033 | 11870 | 2048000 |  | 23898220
2014 | 2014 | February | 2 | 4167100% | 28 | 672 | 3 | 25903 | 26537 | 53074 | 165716 | 246.6012 | 3.1224 | 5314 | 192 | 740 | 24971 | 40582 | 4.0835 | 925.1071 |  | 4752 | 4720 | 11037 | 41990 |  | 6033 | 11870 | 2048000 |  | 23898220
2014 | 2014 | March | 3 | 4169900% | 31 | 744 | 3 | 27256 | 27348 | 54696 | 165716 | 222.7366 | 3.0298 | 5766 | 231 | 722 | 26303 | 41258 | 4.0166 | 879.2258 |  | 4752 | 4720 | 11392 | 41990 |  | 6033 | 11870 | 2048000 |  | 23898220
2014 | 2014 | April | 4 | 4173000% | 30 | 720 | 4 | 31249 | 31317 | 62634 | 189568 | 263.2889 | 3.0266 | 6454 | 253 | 873 | 30123 | 47474 | 3.9931 | 1041.6333 |  | 4590 | 4720 | 13568 | 46444 |  | 5409 | 13340 | 2352000 |  | 38098539
2014 | 2014 | May | 5 | 4176000% | 31 | 744 | 4 | 33546 | 32873 | 65746 | 190394 | 255.9059 | 2.8959 | 6585 | 151 | 897 | 32498 | 50480 | 3.7717 | 1082.129 |  | 4590 | 4720 | 13515 | 46444 |  | 5409 | 13340 | 2352000 |  | 38098539
2014 | 2014 | June | 6 | 4179100% | 30 | 720 | 4 | 30193 | 30544 | 61088 | 176007 | 244.4542 | 2.8812 | 5996 | 110 | 786 | 29297 | 47304 | 3.7208 | 1006.4333 |  | 4590 | 4720 | 12326 | 46444 |  | 5409 | 13340 | 2352000 |  | 38098539
2014 | 2015 | July | 7 | 4182100% | 31 | 744 | 1 | 31913 | 31818 | 63636 | 193977 | 260.7218 | 3.0482 | 6417 | 141 | 891 | 30881 | 48738 | 3.98 | 1029.4516 |  | 4787 | 4819 | 13779 | 43891 |  | 5549 | 7660 | 2459000 |  | 40727344 | 100% | 93.6% | 93.9% | 95% | 99.6%
2014 | 2015 | August | 8 | 4185200% | 31 | 744 | 1 | 29106 | 29247 | 58494 | 174887 | 235.0632 | 2.9898 | 5904 | 266 | 812 | 28028 | 44530 | 3.9274 | 938.9032 |  | 4787 | 4819 | 12018 | 43891 |  | 5549 | 7660 | 2459000 |  | 40727344 | 100% | 93.6% | 93.9% | 95% | 99.6%
2014 | 2015 | September | 9 | 4188300% | 30 | 720 | 1 | 26888 | 26594 | 53188 | 161161 | 223.8347 | 3.03 | 5430 | 349 | 762 | 25777 | 40106 | 4.0184 | 896.2667 |  | 4787 | 4819 | 11009 | 43891 |  | 5549 | 7660 | 2459000 |  | 40727344 | 100% | 93.6% | 93.9% | 95% | 99.6%
2014 | 2015 | October | 10 | 4191300% | 31 | 744 | 2 | 26595 | 27883 | 55766 | 178450 | 239.8522 | 3.2 | 5990 | 521 | 846 | 25228 | 41052 | 4.3469 | 857.9032 |  | 4970 | 4819 | 12745 | 44985 | 677.9 | 5500 | 9630 | 2044000 | 3.2% | 33436464 | 93.8% | 100% | 96.2% | 100% | 100% | 30.5 | 242.2 | 84.2 | 9 | 107.3 | 63 | 85 | 87.8 | 78.5 | 90.6 | 93.5 | 86.7 | 88.8 | 92.4 | 70.3
2014 | 2015 | November | 11 | 4194400% | 30 | 720 | 2 | 26468 | 27099 | 54198 | 172875 | 240.1042 | 3.1897 | 5799 | 764 | 793 | 24911 | 39486 | 4.3781 | 882.2667 |  | 4970 | 4819 | 12276 | 44985 | 677.9 | 5500 | 9630 | 2044000 | 3.2% | 33436464 | 93.8% | 100% | 96.2% | 100% | 100% | 30.5 | 242.2 | 84.2 | 9 | 107.3 | 63 | 81.9 | 85.2 | 74 | 90.5 | 92.6 | 82 | 89.9 | 92.8 | 83.3
2014 | 2015 | December | 12 | 4197400% | 31 | 744 | 2 | 33057 | 30474 | 60948 | 179088 | 240.7097 | 2.9384 | 6123 | 529 | 853 | 31675 | 45938 | 3.8985 | 1066.3548 |  | 4970 | 4819 | 12890 | 44985 | 677.9 | 5500 | 9630 | 2044000 | 3.2% | 33436464 | 93.8% | 100% | 96.2% | 100% | 100% | 30.5 | 242.2 | 84.2 | 9 | 107.3 | 63 | 75.8 | 80.5 | 65.2 | 84.7 | 91.7 | 67.8 | 83.7 | 91 | 65
2015 | 2015 | January | 1 | 4200500% | 31 | 744 | 3 | 28769 | 28114 | 56228 | 167202 | 224.7339 | 2.9736 | 5632 | 389 | 825 | 27555 | 42536 | 3.9308 | 928.0323 |  | 4808 | 4819 | 11777 | 41107 | 676.9 | 5475 | 12990 | 1908000 |  | 24834867
2015 | 2015 | February | 2 | 4203600% | 28 | 672 | 3 | 24308 | 26301 | 52602 | 160221 | 238.4241 | 3.0459 | 5426 | 351 | 794 | 23163 | 39460 | 4.0603 | 868.1429 |  | 4808 | 4819 | 11322 | 41107 | 676.9 | 5475 | 12990 | 1908000 |  | 24834867
2015 | 2015 | March | 3 | 4206400% | 31 | 744 | 3 | 28424 | 27461 | 54922 | 161860 | 217.5538 | 2.9471 | 5428 | 272 | 747 | 27405 | 42028 | 3.8512 | 916.9032 |  | 4808 | 4819 | 11094 | 41107 | 676.9 | 5475 | 12990 | 1908000 |  | 24834867
2015 | 2015 | April | 4 | 4209500% | 30 | 720 | 4 | 31225 | 30646 | 61292 | 179434 | 249.2139 | 2.9275 | 6182 | 613 | 848 | 29764 | 46006 | 3.9002 | 1040.8333 |  | 4710 | 4819 | 12784 | 43162 | 681 | 5477 | 5640 | 2090000 |  | 44595720
2015 | 2015 | May | 5 | 4212500% | 31 | 744 | 4 | 29369 | 31160 | 62320 | 195150 | 262.2984 | 3.1314 | 6701 | 531 | 889 | 27949 | 46078 | 4.2352 | 947.3871 |  | 4710 | 4819 | 11786 | 43162 | 681 | 5477 | 5640 | 2090000 |  | 44595720
2015 | 2015 | June | 6 | 4215600% | 30 | 720 | 4 | 31982 | 31889 | 63778 | 185137 | 257.1347 | 2.9028 | 5987 | 698 | 804 | 30480 | 48800 | 3.7938 | 1066.0667 |  | 4710 | 4819 | 11605 | 43162 | 681 | 5477 | 5640 | 2090000 |  | 44595720
2015 | 2016 | July | 7 | 4218600% | 31 | 744 | 1 | 34196 | 32537 | 65074 | 191850 | 257.8629 | 2.9482 | 6482 | 676 | 895 | 32625 | 48968 | 3.9179 | 1103.0968 |  | 4800 |  | 13358 | 44083 | 678.1 | 5477 | 10510 | 2066000 |  | 42240267 | 94.1% | 97.9% | 98.5% | 99% | 99.1% | 98 | 123.9 | 106.8 | 42.5 | 0 | 32.5 | 84.7 | 89.4 | 75.1 | 89.7 | 92.8 | 85.9 | 87.4 | 91.6 | 82.7
2015 | 2016 | August | 8 | 4221700% | 31 | 744 | 1 | 27869 | 29150 | 58300 | 177256 | 238.2473 | 3.0404 | 6047 | 427 | 780 | 26662 | 43792 | 4.0477 | 899 |  | 4800 |  | 12048 | 44083 | 678.1 | 5477 | 10510 | 2066000 |  | 42240267 | 94.1% | 97.9% | 98.5% | 99% | 99.1% | 98 | 123.9 | 106.8 | 42.5 | 0 | 32.5 | 83.8 | 89.1 | 79.8 | 87.3 | 91.9 | 81.7 | 84.4 | 89.9 | 76.1
2015 | 2016 | September | 9 | 4224800% | 30 | 720 | 1 | 27878 | 26885 | 53770 | 169997 | 236.1069 | 3.1616 | 5633 | 771 | 682 | 26425 | 39598 | 4.2931 | 929.2667 |  | 4800 |  | 11656 | 44083 | 678.1 | 5477 | 10510 | 2066000 |  | 42240267 | 94.1% | 97.9% | 98.5% | 99% | 99.1% | 98 | 123.9 | 106.8 | 42.5 | 0 | 32.5 | 84.4 | 88.8 | 76.9 | 87 | 91 | 75.5 | 86.5 | 90.7 | 11.3
2015 | 2016 | October | 10 | 4227800% | 31 | 744 | 2 | 28047 | 27796 | 55592 | 170190 | 228.75 | 3.0614 | 5807 | 684 | 732 | 26631 | 41146 | 4.1362 | 904.7419 |  |  |  | 11899 | 43757
2015 | 2016 | November | 11 | 4230900% | 30 | 720 | 2 | 25722 | 27510 | 55020 | 165681 | 230.1125 | 3.0113 | 5549 | 676 | 726 | 24320 | 41118 | 4.0294 | 857.4 |  |  |  | 11626 | 43757
2015 | 2016 | December | 12 | 4233900% | 31 | 744 | 2 | 31687 | 30266 | 60532 | 188973 | 253.996 | 3.1219 | 6313 | 787 | 816 | 30084 | 44700 | 4.2276 | 1022.1613 |  |  |  | 13140 | 43757
2016 | 2016 | January | 1 | 4237000% | 31 | 744 | 3 | 26446 | 28091 | 56182 | 168391 | 226.332 | 2.9972 | 5748 | 642 | 740 | 25064 | 41922 | 4.0168 | 853.0968 |  | 4893 |  | 11902 | 41606
2016 | 2016 | February | 2 | 4240100% | 29 | 696 | 3 | 27639 | 26414 | 52828 | 160228 | 230.2126 | 3.033 | 5487 | 850 | 689 | 26100 | 38776 | 4.1321 | 953.069 |  | 4893 |  | 11192 | 41606
2016 | 2016 | March | 3 | 4243000% | 31 | 744 | 3 | 28232 | 27580 | 55160 | 165676 | 222.6828 | 3.0036 | 5632 | 792 | 758 | 26682 | 40796 | 4.0611 | 910.7097 |  | 4893 |  | 11501 | 41606
2016 | 2016 | April | 4 | 4246100% | 30 | 720 | 4 | 29814 | 30356 | 60712 | 188882 | 262.3361 | 3.1111 | 6289 | 996 | 932 | 27886 | 44278 | 4.2658 | 993.8 |  |  |  | 13853 | 47521 |  | 5651 | 11590 | 1794000 |  | 42074659 | 99.5% | 98.8% | 99.1% | 100% | 99.7% | 30.2 | 25.3 | 0 | 6.7 | 0 | 0
2016 | 2016 | May | 5 | 4249100% | 31 | 744 | 4 | 31623 | 31530 | 63060 | 189239 | 254.3535 | 3.0009 | 6380 | 605 | 936 | 30082 | 47218 | 4.0078 | 1020.0968 |  |  |  | 13541 | 47521 |  | 5651 | 11590 | 1794000 |  | 42074659 | 99.5% | 98.8% | 99.1% | 100% | 99.7% | 30.2 | 25.3 | 0 | 6.7 | 0 | 0
2016 | 2016 | June | 6 | 4252200% | 30 | 720 | 4 | 32896 | 31766 | 63532 | 181762 | 252.4472 | 2.861 | 6034 | 661 | 885 | 31350 | 48372 | 3.7576 | 1096.5333 |  |  |  | 12813 | 47521 |  | 5651 | 11590 | 1794000 |  | 42074659 | 99.5% | 98.8% | 99.1% | 100% | 99.7% | 30.2 | 25.3 | 0 | 6.7 | 0 | 0
2016 | 2017 | July | 7 | 4255200% | 31 | 744 | 1 | 29430 | 32121 | 64242 | 191425 | 257.2917 | 2.9797 | 6459 | 504 | 752 | 28174 | 48812 | 3.9217 | 949.3548 |  |  |  | 13363 | 44524 | 685.1 | 5598 | 21430 | 1641000 |  | 45019026 | 97.7% | 94.6% | 98.7% | 100% | 100% | 32.6 | 165.3 | 88.4 | 0 | 0 | 177.3
2016 | 2017 | August | 8 | 4258300% | 31 | 744 | 1 | 31922 | 29593 | 59186 | 188295 | 253.0847 | 3.1814 | 6482 | 642 | 734 | 30546 | 43470 | 4.3316 | 1029.7419 |  |  |  | 13092 | 44524 | 685.1 | 5598 | 21430 | 1641000 |  | 45019026 | 97.7% | 94.6% | 98.7% | 100% | 100% | 32.6 | 165.3 | 88.4 | 0 | 0 | 177.3
2016 | 2017 | September | 9 | 4261400% | 30 | 720 | 1 | 27532 | 26908 | 53816 | 157403 | 218.6153 | 2.9248 | 5366 | 734 | 580 | 26218 | 40456 | 3.8907 | 917.7333 |  |  |  | 10912 | 44524 | 685.1 | 5598 | 21430 | 1641000 |  | 45019026 | 97.7% | 94.6% | 98.7% | 100% | 100% | 32.6 | 165.3 | 88.4 | 0 | 0 | 177.3
2016 | 2017 | October | 10 | 4264400% | 31 | 744 | 2 | 26941 | 27778 | 55556 | 171525 | 230.5444 | 3.0874 | 5734 | 926 | 671 | 25344 | 40894 | 4.1944 | 869.0645 |  | 4878 |  | 12140 | 45907 | 688.3 | 5712 | 10630 | 1740000 |  | 36611403 | 97.9% | 99.6% | 94.3% | 100% | 100% | 9 | 252.5 | 84 | 0 | 0 | 103.7
2016 | 2017 | November | 11 | 4267500% | 30 | 720 | 2 | 26677 | 27525 | 55050 | 170976 | 237.4667 | 3.1058 | 5762 | 941 | 711 | 25025 | 40222 | 4.2508 | 889.2333 |  | 4878 |  | 12229 | 45907 | 688.3 | 5712 | 10630 | 1740000 |  | 36611403 | 97.9% | 99.6% | 94.3% | 100% | 100% | 9 | 252.5 | 84 | 0 | 0 | 103.7
2016 | 2017 | December | 12 | 4270500% | 31 | 744 | 2 | 31030 | 30300 | 60600 | 191612 | 257.543 | 3.1619 | 6457 | 1035 | 781 | 29214 | 44054 | 4.3495 | 1000.9677 |  | 4878 |  | 14219 | 45907 | 688.3 | 5712 | 10630 | 1740000 |  | 36611403 | 97.9% | 99.6% | 94.3% | 100% | 100% | 9 | 252.5 | 84 | 0 | 0 | 103.7
2017 | 2017 | January | 1 | 4273600% | 31 | 744 | 3 | 29185 | 28353 | 56706 | 165770 | 222.8091 | 2.9233 | 5931 | 1083 | 689 | 27413 | 41300 | 4.0138 | 941.4516 |  | 4870 |  | 11933 |  | 678.8 | 5405 | 13390 | 1642000 |  | 29064732
2017 | 2017 | February | 2 | 4276700% | 28 | 672 | 3 | 25769 | 26217 | 52434 | 153757 | 228.8051 | 2.9324 | 5302 | 1413 | 644 | 23712 | 37716 | 4.0767 | 920.3214 |  | 4870 |  | 11067 |  | 678.8 | 5405 | 13390 | 1642000 |  | 29064732
2017 | 2017 | March | 3 | 4279500% | 31 | 744 | 3 | 25814 | 27697 | 55394 | 163200 | 219.3548 | 2.9462 | 5264 | 1291 | 669 | 23854 | 40946 | 3.9857 | 832.7097 |  | 4870 |  | 11355 |  | 678.8 | 5405 | 13390 | 1642000 |  | 29064732
2017 | 2017 | April | 4 | 4282600% | 30 | 720 | 4 | 30677 | 30423 | 60846 | 189608 | 263.3444 | 3.1162 | 6255 | 1420 | 966 | 28291 | 43564 | 4.3524 | 1022.5667 |  | 4946 |  | 13778 | 47923 | 686.4 | 6191 | 13440 | 1234000 |  | 42298090
2017 | 2017 | May | 5 | 4285600% | 31 | 744 | 4 | 32895 | 31350 | 62700 | 191859 | 257.875 | 3.06 | 6285 | 1705 | 945 | 30245 | 44830 | 4.2797 | 1061.129 |  | 4946 |  | 13849 | 47923 | 686.4 | 6191 | 13440 | 1234000 |  | 42298090
2017 | 2017 | June | 6 | 4288700% | 30 | 720 | 4 | 30743 | 31251 | 62502 | 184685 | 256.5069 | 2.9549 | 5911 | 1717 | 894 | 28132 | 45458 | 4.0628 | 1024.7667 |  | 4946 |  | 12998 | 47923 | 686.4 | 6191 | 13440 | 1234000 |  | 42298090
2017 | 2018 | July | 7 | 4291700% | 31 | 744 | 1 | 30914 | 31763 | 63526 | 190170 | 255.6048 | 2.9936 | 6476 | 1807 | 869 | 28238 | 45222 | 4.2053 | 997.2258 |  | 4918 |  | 13182 | 45293 | 683.4 | 5670 | 14240 | 1362000 |  | 40368876
2017 | 2018 | August | 8 | 4294800% | 31 | 744 | 1 | 31668 | 30200 | 60400 | 186971 | 251.3051 | 3.0955 | 6237 | 1836 | 871 | 28961 | 42512 | 4.3981 | 1021.5484 |  | 4918 |  | 12970 | 45293 | 683.4 | 5670 | 14240 | 1362000 |  | 40368876
2017 | 2018 | September | 9 | 4297900% | 30 | 720 | 1 | 27478 | 27060 | 54120 | 167941 | 233.2514 | 3.1031 | 5484 | 1805 | 728 | 24945 | 38086 | 4.4095 | 915.9333 |  | 4918 |  | 11886 | 45293 | 683.4 | 5670 | 14240 | 1362000 |  | 40368876
2017 | 2018 | October | 10 | 4300900% | 31 | 744 | 2 | 26772 | 27869 | 55738 | 175965 | 236.5121 | 3.157 | 5739 | 1638 | 817 | 24317 | 39350 | 4.4718 | 863.6129 |  | 5048 |  | 12417 | 44928 | 688 | 5555 | 16640 | 1340000 |  | 31624142
2017 | 2018 | November | 11 | 4304000% | 30 | 720 | 2 | 25146 | 26359 | 52718 | 155341 | 215.7514 | 2.9466 | 5107 | 1554 | 701 | 22891 | 37994 | 4.0886 | 838.2 |  | 5048 |  | 10777 | 44928 | 688 | 5555 | 16640 | 1340000 |  | 31624142
2017 | 2018 | December | 12 | 4307000% | 31 | 744 | 2 | 29869 | 31594 | 63188 | 196448 | 264.043 | 3.1089 | 6504 | 1339 | 876 | 27654 | 45750 | 4.2939 | 963.5161 |  | 5048 |  | 14606 | 44928 | 688 | 5555 | 16640 | 1340000 |  | 31624142
2018 | 2018 | January | 1 | 4310100% | 31 | 744 | 3 | 30726 | 28181 | 56362 | 181955 | 244.5632 | 3.2283 | 6084 | 1301 | 755 | 28670 | 40082 | 4.5396 | 991.1613 |  | 5088 |  | 12951 | 43065 | 671.3 | 5458 | 9120 | 1358000 |  | 29546941
2018 | 2018 | February | 2 | 4313200% | 28 | 672 | 3 | 25185 | 26407 | 52814 | 162127 | 241.2604 | 3.0698 | 5322 | 884 | 693 | 23608 | 39016 | 4.1554 | 899.4643 |  | 5088 |  | 11120 | 43065 | 671.3 | 5458 | 9120 | 1358000 |  | 29546941
2018 | 2018 | March | 3 | 4316000% | 31 | 744 | 3 | 27770 | 27740 | 55480 | 173819 | 233.6277 | 3.133 | 5823 | 829 | 754 | 26187 | 40668 | 4.2741 | 895.8065 |  | 5088 |  | 12029 | 43065 | 671.3 | 5458 | 9120 | 1358000 |  | 29546941
2018 | 2018 | April | 4 | 4319100% | 30 | 720 | 4 | 32040 | 30420 | 60840 | 190177 | 264.1347 | 3.1259 | 6157 | 886 | 1177 | 29977 | 44400 | 4.2833 | 1068 |  | 4722 |  | 13812 | 45677 | 681.3 | 5510 | 11130 | 1433000 |  | 39987886
2018 | 2018 | May | 5 | 4322100% | 31 | 744 | 4 | 34086 | 31531 | 63062 | 184159 | 247.5255 | 2.9203 | 5979 | 1391 | 1124 | 31571 | 46074 | 3.997 | 1099.5484 |  | 4722 |  | 12833 | 45677 | 681.3 | 5510 | 11130 | 1433000 |  | 39987886
2018 | 2018 | June | 6 | 4325200% | 30 | 720 | 4 | 30038 | 31143 | 62286 | 173950 | 241.5972 | 2.7928 | 5456 | 1161 | 1053 | 27824 | 46946 | 3.7053 | 1001.2667 |  | 4722 |  | 11923 | 45677 | 681.3 | 5510 | 11130 | 1433000 |  | 39987886
2018 | 2019 | July | 7 | 4328200% | 31 | 744 | 1 | 30862 | 31273 | 62546 | 188966 | 253.9866 | 3.0212 | 5989 | 1013 | 1102 | 28747 | 46338 | 4.078 | 995.5484 |  | 4722 |  | 13042 | 41894 | 680.8 | 5503 | 14650 | 1469000 |  | 40348706
2018 | 2019 | August | 8 | 4331300% | 31 | 744 | 1 | 31595 | 30590 | 61180 | 181530 | 243.9919 | 2.9671 | 5808 | 1040 | 1071 | 29484 | 45342 | 4.0036 | 1019.1935 |  | 4722 |  | 12393 | 41894 | 680.8 | 5503 | 14650 | 1469000 |  | 40348706
2018 | 2019 | September | 9 | 4334400% | 30 | 720 | 1 | 27388 | 27141 | 54282 | 145384 | 201.9222 | 2.6783 | 4323 | 1138 | 851 | 25399 | 41658 | 3.4899 | 912.9333 |  | 4722 |  | 9490 | 41894 | 680.8 | 5503 | 14650 | 1469000 |  | 40348706
2018 | 2019 | October | 10 | 4337400% | 31 | 744 | 2 | 27438 | 27584 | 55168 | 168116 | 225.9624 | 3.0473 | 5173 | 1108 | 1001 | 25329 | 40604 | 4.1404 | 885.0968 |  | 4788 |  | 11381 | 42509 | 664 | 5602 | 14340 | 1515000 |  | 29037973
2018 | 2019 | November | 11 | 4340500% | 30 | 720 | 2 | 27102 | 26367 | 52734 | 152101 | 211.2514 | 2.8843 | 4909 | 992 | 928 | 25182 | 39076 | 3.8924 | 903.4 |  | 4788 |  | 10268 | 42509 | 664 | 5602 | 14340 | 1515000 |  | 29037973
2018 | 2019 | December | 12 | 4343500% | 31 | 744 | 2 | 28150 | 31633 | 63266 | 189225 | 254.3347 | 2.9909 | 6273 | 933 | 1097 | 26120 | 46660 | 4.0554 | 908.0645 |  | 4788 |  | 13770 | 42509 | 664 | 5602 | 14340 | 1515000 |  | 29037973
2019 | 2019 | January | 1 | 4346600% | 31 | 744 | 3 | 26808 | 28251 | 56502 | 172350 | 231.6532 | 3.0503 | 5696 | 964 | 1029 | 24815 | 41124 | 4.191 | 864.7742 |  | 4873 |  | 12314 | 41894 | 681 | 5496 | 8420 | 1588000 |  | 27065631
2019 | 2019 | February | 2 | 4349700% | 28 | 672 | 3 | 26342 | 25895 | 51790 | 149123 | 221.9092 | 2.8794 | 5218 | 743 | 891 | 24708 | 38086 | 3.9154 | 940.7857 |  | 4873 |  | 10284 | 41894 | 681 | 5496 | 8420 | 1588000 |  | 27065631
2019 | 2019 | March | 3 | 4352500% | 31 | 744 | 3 | 29157 | 28179 | 56358 | 173288 | 232.914 | 3.0748 | 5873 | 885 | 936 | 27336 | 40970 | 4.2296 | 940.5484 |  | 4873 |  | 12333 | 41894 | 681 | 5496 | 8420 | 1588000 |  | 27065631
2019 | 2019 | April | 4 | 4355600% | 30 | 720 | 4 | 33904 | 30387 | 60774 | 179676 | 249.55 | 2.9565 | 6503 | 895 | 967 | 32042 | 44044 | 4.0795 | 1130.1333 |  | 4608 |  | 12894 | 44256 | 687.4 | 5553 | 9650 | 1421000 |  | 40434486
2019 | 2019 | May | 5 | 4358600% | 31 | 744 | 4 | 31913 | 31567 | 63134 | 171814 | 230.9328 | 2.7214 | 5670 | 1038 | 922 | 29953 | 47874 | 3.5889 | 1029.4516 |  | 4608 |  | 11674 | 44256 | 687.4 | 5553 | 9650 | 1421000 |  | 40434486
2019 | 2019 | June | 6 | 4361700% | 30 | 720 | 4 | 27793 | 31190 | 62380 | 180750 | 251.0417 | 2.8976 | 5633 | 1029 | 961 | 25803 | 47134 | 3.8348 | 926.4333 |  | 4608 |  | 12587 | 44256 | 687.4 | 5553 | 9650 | 1421000 |  | 40434486
2019 | 2020 | July | 7 | 4364700% | 31 | 744 | 1 | 32440 |  | 0 |  | 0 | #DIV/0! |  |  |  | 32440 | 0 | #DIV/0! | 1046.4516
2019 | 2020 | August | 8 | 4367800% | 31 | 744 | 1 | 28979 |  | 0 |  | 0 | #DIV/0! |  |  |  | 28979 | 0 | #DIV/0! | 934.8065
2019 | 2020 | September | 9 | 4370900% | 30 | 720 | 1 | 27634 |  | 0 |  | 0 | #DIV/0! |  |  |  | 27634 | 0 | #DIV/0! | 921.1333
2019 | 2020 | October | 10 | 4373900% | 31 | 744 | 2 | 29541 |  | 0 |  | 0 | #DIV/0! |  |  |  | 29541 | 0 | #DIV/0! | 952.9355
2019 | 2020 | November | 11 | 4377000% | 30 | 720 | 2 | 26324 |  | 0 |  | 0 | #DIV/0! |  |  |  | 26324 | 0 | #DIV/0! | 877.4667
2019 | 2020 | December | 12 | 4380000% | 31 | 744 | 2 | 29487 |  | 0 |  | 0 | #DIV/0! |  |  |  | 29487 | 0 | #DIV/0! | 951.1935
2020 | 2020 | January | 1 | 4383100% | 31 | 744 | 3 | 30781 |  | 0 |  | 0 | #DIV/0! |  |  |  | 30781 | 0 | #DIV/0! | 992.9355
2020 | 2020 | February | 2 | 4386200% | 29 | 696 | 3 | 25371 |  | 0 |  | 0 | #DIV/0! |  |  |  | 25371 | 0 | #DIV/0! | 874.8621
2020 | 2020 | March | 3 | 4389100% | 31 | 744 | 3 | 25939 |  | 0 |  | 0 | #DIV/0! |  |  |  | 25939 | 0 | #DIV/0! | 836.7419
2020 | 2020 | April | 4 | 4392200% | 30 | 720 | 4 | 29309 |  | 0 |  | 0 | #DIV/0! |  |  |  | 29309 | 0 | #DIV/0! | 976.9667
2020 | 2020 | May | 5 | 4395200% | 31 | 744 | 4 | 32745 |  | 0 |  | 0 | #DIV/0! |  |  |  | 32745 | 0 | #DIV/0! | 1056.2903
2020 | 2020 | June | 6 | 4398300% | 30 | 720 | 4 | 33207 |  | 0 |  | 0 | #DIV/0! |  |  |  | 33207 | 0 | #DIV/0! | 1106.9
2020 | 2021 | July | 7 | 4401300% | 31 | 744 | 1 | 27169 |  | 0 |  | 0 | #DIV/0! |  |  |  | 27169 | 0 | #DIV/0! | 876.4194
2020 | 2021 | August | 8 | 4404400% | 31 | 744 | 1 | 32698 |  | 0 |  | 0 | #DIV/0! |  |  |  | 32698 | 0 | #DIV/0! | 1054.7742
2020 | 2021 | September | 9 | 4407500% | 30 | 720 | 1 | 30282 |  | 0 |  | 0 | #DIV/0! |  |  |  | 30282 | 0 | #DIV/0! | 1009.4
2020 | 2021 | October | 10 | 4410500% | 31 | 744 | 2 | 27642 |  | 0 |  | 0 | #DIV/0! |  |  |  | 27642 | 0 | #DIV/0! | 891.6774
2020 | 2021 | November | 11 | 4413600% | 30 | 720 | 2 | 24659 |  | 0 |  | 0 | #DIV/0! |  |  |  | 24659 | 0 | #DIV/0! | 821.9667
2020 | 2021 | December | 12 | 4416600% | 31 | 744 | 2 | 31336 |  | 0 |  | 0 | #DIV/0! |  |  |  | 31336 | 0 | #DIV/0! | 1010.8387
2021 | 2021 | January | 1 | 4419700% | 31 | 744 | 3 | 27234 |  | 0 |  | 0 | #DIV/0! |  |  |  | 27234 | 0 | #DIV/0! | 878.5161
2021 | 2021 | February | 2 | 4422800% | 28 | 672 | 3 | 24563 |  | 0 |  | 0 | #DIV/0! |  |  |  | 24563 | 0 | #DIV/0! | 877.25
2021 | 2021 | March | 3 | 4425600% | 31 | 744 | 3 | 31207 |  | 0 |  | 0 | #DIV/0! |  |  |  | 31207 | 0 | #DIV/0! | 1006.6774
2021 | 2021 | April | 4 | 4428700% | 30 | 720 | 4 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2021 | 2021 | May | 5 | 4431700% | 31 | 744 | 4 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2021 | 2021 | June | 6 | 4434800% | 30 | 720 | 4 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2021 | 2022 | July | 7 | 4437800% | 31 | 744 | 1 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2021 | 2022 | August | 8 | 4440900% | 31 | 744 | 1 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2021 | 2022 | September | 9 | 4444000% | 30 | 720 | 1 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2021 | 2022 | October | 10 | 4447000% | 31 | 744 | 2 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2021 | 2022 | November | 11 | 4450100% | 30 | 720 | 2 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2021 | 2022 | December | 12 | 4453100% | 31 | 744 | 2 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2022 | January | 1 | 4456200% | 31 | 744 | 3 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2022 | February | 2 | 4459300% | 28 | 672 | 3 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2022 | March | 3 | 4462100% | 31 | 744 | 3 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2022 | April | 4 | 4465200% | 30 | 720 | 4 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2022 | May | 5 | 4468200% | 31 | 744 | 4 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2022 | June | 6 | 4471300% | 30 | 720 | 4 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2023 | July | 7 | 4474300% | 31 | 744 | 1 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2023 | August | 8 | 4477400% | 31 | 744 | 1 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2023 | September | 9 | 4480500% | 30 | 720 | 1 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2023 | October | 10 | 4483500% | 31 | 744 | 2 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2023 | November | 11 | 4486600% | 30 | 720 | 2 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2022 | 2023 | December | 12 | 4489600% | 31 | 744 | 2 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2023 | 2023 | January | 1 | 4492700% | 31 | 744 | 3 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2023 | 2023 | February | 2 | 4495800% | 28 | 672 | 3 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2023 | 2023 | March | 3 | 4498600% | 31 | 744 | 3 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2023 | 2023 | April | 4 | 4501700% | 30 | 720 | 4 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2023 | 2023 | May | 5 | 4504700% | 31 | 744 | 4 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
2023 | 2023 | June | 6 | 4507800% | 30 | 720 | 4 |  |  | 0 |  | 0 | #DIV/0! |  |  |  | 0 | 0 | #DIV/0! | 0
Formulas:
Days = DAY(EOMONTH(DATE(Table1[[#This Row],[Calendar Year]],Table1[[#This Row],[MonthNum]],1),0))
Note on W95: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Q2FY18 Report Page 14 says this should be 5142 Btu/lb